# G18 Appendix 2 PORTABLE APPLIANCE INSPECTION AND TEST CHECKLIST AND RECORD SHEET

| Item | Pass Condition |
| --- | --- |
| Mains Lead | Two layers of insulation on all parts outside plug and case. |
|  | No cuts, cracks, kinks, fraying or taped repairs. |
|  | Cable protected by grommet or other means at entry point to equipment. |
|  | No appreciable movement of lead at entry point to equipment. |
| Mains Plug | Body not damaged. |
|  | Sleeved pins fitted where children are present. |
|  | Cable sheath gripped securely. |
|  | Correct fuse fitted. |
|  | Correctly connected (re-wireable units). |
|  | Wires secure in pins (re-wireable units). |
|  | Cover securely attached. |
| Mains Lead Equipment Connector (if lead is detachable) and sockets on extension leads | Body not damaged. Unable to open without a tool. Cable sheath gripped securely. |
| Equipment Male Connector (if lead is detachable) | Pins straight and in good condition. |
| Mains on/off Switch | No damage and correct operation. |
| Class 1 Equipment | Case not damaged, vents clear of dust and dirt. |
|  | Earth resistance less than 0.1 or 0.5 if fused at 3A or less. |
|  | Insulation resistance above 2M. |
| Class 2 Equipment | Case not damaged, vents clear of dust and dirt. |
|  | Insulation resistance above 7M. |
| Accessible Fuse Holders | No damage. |
|  | Removal of carrier does not permit live parts to be touched. |
| Exposed Output Connections | No voltage greater than 50V. |

## INSPECTION AND TEST CHECKLIST

## PORTABLE APPLIANCE INSPECTION AND TEST RECORD SHEET

| ### Date | ### Sheet of |
| --- | --- |
| ## ESTABLISHMENT |  |
| ## PERSON CARRYING OUT INSPECTIONS AND TESTS |  |

| ### Location | ### Equip No. | ### Description | ### Class | ### *Pass/Fail | ### Comments |
| --- | --- | --- | --- | --- | --- |
|  | 1 |  |  |  |  |
|  | 2 |  |  |  |  |
|  | 3 |  |  |  |  |
|  | 4 |  |  |  |  |
|  | 5 |  |  |  |  |
|  | 6 |  |  |  |  |
|  | 7 |  |  |  |  |
|  | 8 |  |  |  |  |
|  | 9 |  |  |  |  |
|  | 10 |  |  |  |  |
|  | 11 |  |  |  |  |
|  | 12 |  |  |  |  |
|  | 13 |  |  |  |  |
|  | 14 |  |  |  |  |
|  | 15 |  |  |  |  |
|  | 16 |  |  |  |  |
|  | 17 |  |  |  |  |